## Method Statement – SC021&SC038 – Cleanroom & Other Modular rooms Assembly Activities Rev B

### 1. Project Details

- Project Name: [Sumitumo Cable Factory Installation]

- Location: [Nigg, B9175, Cromarty, Highland, Scotland, IV19 1QY, United Kingdom]

- Main Contractor: [Europlan]

- Subcontractor (Assembly Works): [Europlan]

- Prepared by: [Hemant Apte]

- Date: [17/07/2026]

### 2. Scope of Work

This method statement outlines the procedure for the safe and efficient Cleanroom Assembly Activities including:

- Setting out Modular Room base.

- Assembling Columns, Walls, Doors, Windows & Openings

- Assembling Ceiling Grid.

- Installation of FFUs (where applicable)

- Installation of Air Ducting. (where applicable)

- Installation of Underfloor SFX Insulation and final flooring boards (where applicable)

- Connections of vendor pre-wired services.

### 3. Responsibilities

- Project Manager: Ensure overall planning, coordination, and resource management.

- Site Engineer: Supervise electrical work and ensure compliance with specifications.

- Foreman: Direct onsite activities and ensure safety compliance.

- Electricians: Perform tasks according to drawings and safety procedures.

- Safety Officer: Monitor implementation of safety measures.

- All personnel must have appropriate training and certification for the works being carried out, such as CPCS, SSSTS, SMSTS, NPORS etc.

### 4. Materials and Equipment

- Electrical / Battery operated hand tools

- Electrical Work bench tools (Chop Saw, Band Saw)

- Non powered hand tools (Pliers, Screwdrivers, Spanners, Knives)

- Elevated work platforms (Mobile aluminium Scaffold tower,

- Topple Arrest Arrangements

- Scissor Lifts

- Temporary Lighting

- Lifter frames for lifting ceiling trusses, ducting

- Galizia Pick & Carry Crane with Mini-clad vacuum lifter (for more than 4.5m high 1st and 2nd floor clean room installation)

- Prefabricated Modular Cleanroom components.

- Unistrut and accessories

- Scaffolding

- PPE (standard site requirements & task specific)

### 5. Method of Work

Installation sequence provided in the Vendor’s ‘General Installation Manual for FastIns Modular Cleanroom Castle™’ is for guidance only and shall be adopted to actual site condition and site construction sequences and local construction and safety regulations.

#### 5.1 Site Preparation and Setting Out

- Inspect floor slab for level tolerance, cleanliness and load capacity. Mark cleanroom footprint using approved drawings and laser level.

- Estimated Fully Assembled weights of Rooms.

| Room Name or Floor | Weight (kg) |
| --- | --- |
| SC021 CLEANROOMS |  |
| GF CLEANROOM | 5600 |
| FF/F1 CLEANROOM | 22000 |
| SF/F2 CLEANROOM | 13500 |
| SC038 MODULAR ROOMS |  |
| ROOM-A +ROOM B | 12000 |
| ROOM C | 7600 |
| ROOM CCT | 4500 |
| ROOM FJA | 6000 |
| ROOM LPR | 3000 |
| ROOM DC | 950 |
| TOILET BLOCK 01 (1.1 L+1.2R)- MF | 950 |
| TOILET BLOCK 02 – MF | 950 |
| TOILET BLOCK 03 – MF | 950 |
| TOILET BLOCK 04 – MF | 950 |
| TOILET BLOCK 05 – VCB | 1150 |

#### 5.2 Base Frame Installation

- Install and level base frames in accordance with manufacturer layout and assembly drawings.

- Secure joints using approved fixings.

- Secure the frame to the floor with provided anchor bolts.

#### 5.3 Columns , Wall Panels, Windows, Doors & Openings

- It is recommended by manufacturer to start the assembly of the modular cleanroom at any corner based on site assessment, preferably where the shortest length panel top rail is required in any direction. After securing a corner assembly installation of wall panels shall further continue in sections which are connecting to MAIN GRID.

- Based on the orientation of MAIN GRID BEAMS assembly of walls and columns connecting to the MAIN BEAMS shall be progressed parallelly in sections which will ensure the top side of the panels is tied off securely during installation.

- During installation of wall panels and columns until such time MAIN GRID BEAM can be securely installed a temporary topple arrest arrangement shall be provided from existing building members, where available, as per site requirement not exceeding after 3 (four) panel assembly wide spans fitted with full length WALL TOP GRID BEAM to prevent any accidental topple of panel/s till full structural integrity is achieved for the structure.

- In an event there are no existing building members available with in vicinity temporary scaffolding support, and or temporary Panel Top/ Ceiling Grid Beam in full lengths with added subframes in line with adjacent wall assembly or L or C Shaped frame shall be utilised along with the modular room spare column.

- For purposes of understanding the requirements of manual handling following weights shall be used as a guidance for allocation of resources.

  - Weight of single wall panel for 1.2m wide 4.0m long shall be 75kgs in total.

  - Weight of single wall panel for 1.2m wide 5.50m long shall be 95kgs in total.

  - Weight of single wall panel for 1.2m wide 7.50m long shall be 140 kgs in total.

- It is highly recommended to use appropriate lifting and moving machine (Galizia Pick & Carry Crane with Mini-clad vacuum lifter) to install wall panels over 4.5m length.

- Manually attached suckers to be utilised for panels under 4.5 metres.

- Protective film to be removed to ensure maximum suction and a secure grip.

#### 5.4 Ceiling Grid Installation

- Install main grid beams these are factory spliced long grid beams between opposite side wall panels. Install at least one runs of main grid beam before commencement of sub-grid beams installation.

- Sub grid beams are short length beams usually placed between two main grid beams or between main grid beam and wall top beam.

- Install reinforcement trusses as per manufacturer’s drawings and secure as per manufacturer’s details.

#### 5.5 FFU Installation in Ceiling Grid (Applicable for cleanrooms only)

- Install FFUs in the ceiling grid as per detail provided by the manufacturer.

#### 5.6 Air Ducting Installation (Applicable for cleanrooms only)

- Install supply and return air ducts as per manufacturer’s drawings where applicable.

- Based on the access to the installation flange connections for the ducting sections can be prepared before lifting the ducting in its’ final installation position.

- Access to ducting installation can be achieved through the ceiling grid openings.

- In an event a personal access is required for any activities to be performed above cleanroom ceilings such access shall ensure secured installation of all columns, walls, ceiling grid beams, sub ceiling grid beams, trusses, FFUs & ceiling tiles.

- Walking or standing Access over FFUs is not permitted.

- Manufacture’s Room design is capable of handling not exceeding 85kg slow moving human weight including tools and tackles over the completed ceiling with additional safety and security measures as per site requirements, only and only if there is adequate head room is available for comfortable access, ingress and movements is achievable.

- Appropriate local safety stands shall be adopted for fall arrest and other working at height requirements in case of above room ceiling human access.

#### 5.7 Installation of underfloor SFX Insulation and Final Flooring boards (for Room A, Room B, Room C, Room CCT, Room LPR Only)

- Prepare area free from any loose objects or dirt.

- Install DPM sheet on the existing floor raise along the wall till height of under floor insulation thickness.

- Install underfloor insulation with the recommended 10mm gap from all edges rather than flushing to the walls. Insulation blocks shall be taped to maintain moisture barrier and insulation.

- Pre-floorboard layer sheet to be laid over the insulation.

- Install final floorboard over the insulation in slide and click manner with the recommended 10mm gap from all edges rather than flushing to the walls.

- Install coving on the wall side with flush to flooring.

- For internal steps around door areas, finish the vertical face of insulation with the final floorboard, coving and L trims.

This is applicable for Room A+B, Room, C, Room CCT, Room LRP only.

#### 5.8 Connections of Vendor’s pre-wired services

- Make interconnections of FFUs, Lighting and other pre-wired services as per details provided by the manufacturer.

### 6. Safety and Environmental Controls

- All personnel must wear appropriate PPE High Vis Long Sleeved Jacket/Vest, Hi Vis Trousers (Fluorescent Yellow), Safety Gloves (Minimum cut level 5), Light eye protection, upgraded to impact goggles or full-face visor where RA requires, Safety Boots (with ankle support, steel toecaps, and protective midsoles – no rigger boots allowed)

- Control Measure procedures to be adhered to.

- Proper disposal of any metal cuttings and packaging.

### 7. Emergency Procedures

- Emergency contact list available onsite.

- First aid kits available and accessible in welfare units, site notice boards and offices.

- In case of an electrical shock, power should be isolated / shut off and first aid administered immediately after proven safe to do so.

### 8. Quality Assurance

- All work to be done as per project specifications and installed to BS7671 electrical regulations (e.g., IEC, NEC, or local code).

- Inspection and approval by Vendor representative & QA/QC Engineer before concealment.

### 9. References

- SC021- Cleanroom drawings and specifications

- Site HSE Plan

- Manufacturer’s Installation Guidelines: General Installation Manual for FastIns Modular Cleanroom Castle™. (same applies to Modular rooms for the project)

- Vendor provided Assembly drawings

  - Assembly Drawing for F2(SF) with Truss.pdf

  - Assembly Drawing for F1(FF) with Truss.pdf

  - Assembly Drawing for GF with Truss.pdf

  - Assembly Drawing for Room A+B with Truss.pdf

  - Assembly Drawing for Room C with Truss.pdf

  - Assembly Drawing for Room FJA with Truss.pdf

  - Assembly Drawing for Room CCT with Truss.pdf

  - Assembly Drawing for Room LPR with Truss.pdf

  - Assembly Drawing for Toilet#1 with Truss.pdf

  - Assembly Drawing for Toilet#2 with Truss.pdf

  - Assembly Drawing for Toilet#3 with Truss.pdf

  - Assembly Drawing for Toilet#4 with Truss.pdf

  - Assembly Drawing for Toilet#5 with Truss.pdf

| Operative Name | Signature | Date |
| --- | --- | --- |
| Connor Macphee |  |  |
| William Robertson |  |  |
| Frank Sutherland |  |  |
| Donald |  |  |
| Steven |  |  |
| Rory |  |  |
| Jordan |  |  |
| Lewis Macleod |  |  |
| Wayne Tamplin |  |  |
| Stuart |  |  |
| Craig |  |  |
| Hemant Apte |  |  |